SECTION 235216 - CONDENSING BOILERS

Revise this Section by deleting and inserting text to meet job specific requirements.

GENERAL

SUMMARY

Section includes gas-fired, fire-tube condensing boilers, trim, and accessories for generating hot water.

ACTION SUBMITTALS

Product Data: For each type of product.

Shop Drawings: For boilers, boiler trim, and accessories. Include product description, model number, dimensions, clearances, weights, components and options.

Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Include diagrams for power, signal, and control wiring.

Schematic wiring diagram of boiler control system of the ladder-type showing all components, interlocks, etc. Schematic wiring diagram shall clearly identify factory wiring and field wiring by others.

Detail wiring for power, signal, and control systems.

INFORMATIONAL SUBMITTALS

Retain Seismic options below as required by the jobsite.

Seismic Calculations

Source quality-control reports.

Field quality-control reports.

Manufacturer’s Certification: The boiler manufacturer shall certify the following:

The products and systems furnished are in strict compliance with the specifications.

The boiler, burner, and other associated mechanical and electrical equipment have been properly coordinated and integrated to provide a complete and operable boiler package.

ASME Certification in the form of ASME Stamp on the product and completed and signed data sheet.

ASME CSD-1 Certification, in the form of completed data sheet.

cULus Certification in the form of an affixed label to the equipment.

The specified factory tests have been satisfactorily performed.

The specified field tests have been satisfactorily performed.

CLOSEOUT SUBMITTALS

Operation and maintenance data.

Manufacturer’s printed operation and maintenance manuals shall be submitted prior to final acceptance by the engineer. Operation and maintenance manuals shall contain dimension and wiring drawings, product data, operating instructions, cleaning procedures, replacement parts list, maintenance and repair data, complete parts list, etc.

Manufacturer’s data reports.

Start-up reports.

WARRANTY

The below warranties are specific to the CFC-E product. If equipment warranties are critical to the owner, discuss the extensive CFC-E warranty compared to industry standards and competition. Review specific job warranty requirements with owner, and overall project requirements.

Manufacturer's Warranty: Manufacturer agrees to repair or provide replacement components of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components specified.

Warranty Period for Fire-Tube Condensing Boilers:

The pressure vessel shall be guaranteed against thermal shock for 20 years when utilized in a closed loop hydronic heating system with a temperature differential of 120 °F or less.  The boiler pressure vessel shall be guaranteed accordingly without a minimum flow rate or return water temperature requirement.  The boiler shall not require the use of flow switches or other devices to ensure minimum flow.

The pressure vessel, tubes and tube sheets (heat exchanger) shall be guaranteed against flue gas corrosion and materials/workmanship for a period of 10 years. The condensate collection box shall be guaranteed for 20 years.  The burner cylinder shall be warranted for a period of 5 years.

All parts not covered by the above warranties shall carry a 1 year warranty from startup, or 18 months from shipment, whichever occurs first.  This shall include all electrical components and burner components.

PERFORMANCE REQUIREMENTS

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

ASME Compliance: Fabricate and label boilers to comply with the current version of the ASME Boiler and Pressure Vessel Code.

ASHRAE/IES 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

AHRI Testing: The boilers shall be tested and certified per AHRI requirements for efficiency ratings.

UL Compliance: Test boilers for compliance with UL 795 and CAN1-3.1-77. Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

CSA or cULus certified as an indirect or direct vent boiler and comply with standard CAN1-3.1-77.

Boiler and controls shall be compliant with ASME CSD-1 Code requirements.

Retain "Seismic Fabrication Requirements" Subparagraph below for projects in seismic areas. Mounting Base:

For securing boiler to concrete base.

Seismic Fabrication Requirements: Fabricate mounting base and attachment to boiler pressure vessel, accessories, and components with reinforcement strong enough to withstand seismic forces as required for jobsite when mounting base is anchored to building structure. The boiler manufacturer shall provide required anchoring provisions. Contractor shall anchor boilers to meet specification requirements.

PRODUCT

HIGH MASS FIRETUBE STAINLESS STEEL CONDENSING BOILERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by the following available manufacturer offering products that may be incorporated into the Work shall include, but are not limited to, the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Subject to compliance with requirements, provide Cleaver Brooks Clearfire Boiler(s) model CFC-E as indicated on Drawings or approved equal:

Cleaver Brooks – Model Clearfire CFC-E (Basis of Design)

Bosch/Buderus model SB625

Viessmann Vitocrossal 300 model CT3

"Near condensing" copper fin designs, watertube, cast iron, cast aluminum, or "add-on" secondary condensing exchangers will not be considered. Boilers with minimum flow requirements also will not be considered.

Description: Each unit shall be a down-fired firetube type complete with burner and automatic controls.  The boiler, with all piping and wiring, shall be a factory package.  Each boiler shall be neatly finished, thoroughly tested and properly packaged for shipping.  Boiler design and construction shall be in accordance with Section IV of the ASME Code for hot water heating boilers with a maximum working pressure of 125 PSIG.

Duplex stainless steel has superior corrosion resistance, and minimal thermal stresses compared to other grades of stainless steel.

Heat Exchanger: Duplex stainless steel tubes, tube sheets, and combustion chamber. The heat exchanger shall be a single-pass, counter-flow arrangement.

The firetubes shall be duplex stainless steel, fitted with aluminum internal heat transfer fins.

Pressure Vessel: Carbon steel with welded heads and tube connections.

The boiler shall have one supply connection with dual return water connections. The dual return water connections shall enable the boiler to operate in a condensing mode when as little as 10% of the flow is returned to the low temperature return with a maximum temperature of 120°F.

Water volume is crucial to the boiler’s ability to handle varying flow conditions and reduce cycling. Low water volume boilers are more susceptible to short cycling, and nuisance trips. They often have minimum and maximum flow requirements to protect the heat exchanger.

The boiler pressure vessel shall have a minimum of 50 gallons of water volume/1000 MBH input.

Many condensing boilers have minimum flow requirements. When designing a system, make sure all specified boilers can handle system design conditions.

The boiler shall be low flow tolerant without minimum flow requirements or the use of a flow switch.

Effective fireside heating surface has a direct correlation to the ability of the boiler to condense over a wide range of operating conditions. Since moisture in the flue gases condense on the surface of the tubes, greater amounts of fireside heating surface give the flue gases a larger area to condense on, leading to more efficient operation.

The boiler shall have a minimum of 240 sqft/1000 MBH of effective fireside heating surface.

If jobsite altitude exceeds 2000 ft ASL review equipment capacity and requirements with local Cleaver Brooks representative. Select natural gas or propane gas.

Burner: [Natural] [Propane] gas, forced draft burner mounted in and integral with the boiler hinged top door so when the door is opened the burner head, furnace, tubesheet, and tube entrances are exposed.  The burner door shall utilize easy removable threaded handles, and the burner shall swing upward on gas assist piston arms, one on each side to provide open support of the burner assembly.

The burner shall be a linkage-less, self-regulating, air-fuel ratio gas valve-venturi system.   Burner regulation shall be accomplished without the use of fuel/air mixing valves or actuators.

The burner shall be achieve sub 20 ppm NOx when firing on natural gas at all firing rates.

Burner and fireside access shall be able to be performed by one service technician.

Burner Head: shall be constructed of a stainless steel metal fiber for solid body radiation of the burner flame. Combustion shall take place on the surface of the burner mantle, which shall be constructed of a woven stainless steel metal fabric resulting a 360 degree low temperature radiant flame.

Burner shall be minimum 5:1 fully modulating turndown. (Natural gas)

Burner shall maintain no more than 7% O2 levels throughout the firing rate without additional sensors, linkages, or controls.

The pre-mix design shall utilize a variable speed fan connected to a venturi to simultaneously modulate the fuel and air for a minimum of 5:1 turndown. The valve-venturi design shall also act as a method for compensating for changes in barometric pressure, temperature, and humidity so the excess air levels are not adversely affected by changes in atmospheric conditions. External linkages, damper motor drives and single speed fans shall not be acceptable.

Blower: Centrifugal fan to operate during each burner firing sequence and to prepurge and postpurge the combustion chamber.

The blower motor shall have a variable speed ECM motor with integrated drive electronics. Constant speed motors and variable frequency AC drives are not acceptable.

Gas Train: The gas train shall meet the requirements of CSA/UL and ASME CSD-1 and shall include:

- Low Gas Pressure Interlock, manual reset.

- High Gas Pressure Interlock, manual reset.

- Upstream and downstream manual test cocks.

- Ball Type manual shutoff valve upstream of the main gas valve.

- Unibody double safety gas valve assembly.

- Gas Pressure Regulator

- Union connection to permit burner servicing.

Ignition: Spark ignition with 100 percent main-valve shutoff with UV scanner for flame supervision.

Combustion air proving switch shall be furnished to ensure sufficient combustion airflow is present for burner ignition firing.

To ensure that the flue is not blocked, the burner shall include a High Air Pressure Switch sensing the outlet pressure connection relative to stack backdraft.

Casing:

### Jacket: 18 gauge metal cabinet with snap-in or interlocking closures.

Control Compartment Enclosures: NEMA 250, Type 1A.

Finish: Powder-coated protective finish.

Insulation: Minimum 2-inch thick, mineral-fiber insulation surrounding the heat exchanger.

CFC-E boilers come standard with direct vent connection for ducted combustion air, or room air can be utilized. For room air and direct vent, the combustion air filter kit can be used.

Combustion-Air Connections: Inlet and vent duct collars.

[Combustion air inlet filter]

TRIM

Items A through F below are standard. Select other options as required for specific jobsite or Code requirements.

Safety valve(s) shall be ASME Section IV approved side outlet type mounted on the boiler air vent outlet.  Size shall be in accordance with code requirements and set to open at [30] [50] [60] [75] [80] [90] [100] [125] psig.

Temperature and pressure gauge shall be mounted on the water outlet.

Solid State Low water cut-off probe control with manual reset and test switch.

Manual Reset High Limit Temperature sensor; range not to exceed 210 deg F and shall be an integral device of the Boiler Burner Control and UL Recognized as a limit control.

Outlet water supply sensing probe for operating water limit setpoint.

Return water-sensing probe for operating limit setpoint.

Drain valve

Automatic air vent

Auxiliary low water cutoffs are rarely required for hot water boilers. Review and include only if required for specific jobsite or Code requirements.

Auxiliary low water cutoff

The Cleaver-Brooks Falcon controls have visual indication and audible alarm standard. Only include this option if required for specific jobsite or Code requirements. Falcon audible alarm is 85dBA, separate horn is 100 dBA.

Alarm lights and horn (general alarm light – red, fuel valve light – green, load demand light – white, low water light - amber)

Alarm horn (electronic sounder)

Stack temperature sensor – UL Recognized as a limit control.

The condensate treatment tube is rated for capacities up to 1000 MBH. The tank and combo tank/trap are each rated for 8000 MBH total. The boiler must be on a housekeeping pad to use the combination tank/trap option. Multiple boiler condensate drains can be combined into one tank (or tank/trap) as long as they do not exceed the rated capacity.

Condensate neutralization kit [tube] [tank] [combination tank and trap]

If the system is piped primary only, consider providing the automatic isolation valves as a factory option. If by others, delete the below item.

Automatic isolation valve, including valve, actuator, and transformer to power isolation valve through the boiler. The valve, actuator, and transformer shall ship loose for field installation and wiring.

The isolation valve shall be Bray 2-way resilient seated butterfly valve, model ABL or approved equal, with ANSI 150# flanges, lugged style.

The electric actuator shall a Bray Commercial actuator, or approved equal, 24VAC, fail in position, with auxiliary end switch.

CONTROLS

The Boiler shall include a Falcon Computerized Boiler Burner control which shall be an integrated, solid state digital micro-processing modulating device, complete with sequence indication, fault reset, mode selection, and parameter set-point.  It shall be mounted at the front of the boiler panel for easy access and viewing.

Controller shall provide for both flame safeguard and boiler control through separate power supplied CPU’s (to meet NFPA) and shall perform the following functions:

Burner sequencing with safe start check, pre-purge, Electronic direct spark ignition and post purge. A UV scanner shall be used to prove combustion.

Flame Supervision.  The control shall provide pre-purge and post-purge and shall maintain a running history of operating hours, number of cycles, and the most recent fifteen lockouts.  The control shall be connected to a touchscreen display interface that will display this information in clear English text descriptions.

Safety Shutdown with display of lockout or hold condition.

PID modulating control of the variable speed fan for firing capacity relative to load requirements; i.e. to meet supply water temperature set point.

Gas pressure supervision, high and low.

Combustion Air Proving Supervision.

High Air Pressure [back draft too high] Supervision.

The supply temperature and set-point temperature shall be displayed at all times on the touch screen display.

Controller shall be equipped with a touch screen display for set up, trouble shooting, and operational display, and shall include ModBus communication capability of this information.

Include the programming of circulating pump or isolation valve control and support the control of 2 heating demand loops.

All parameter input control set-points shall be factory pre-configured. Parameter settings are to be established to suit jobsite conditions -- settings are to be configured at the time of initial jobsite operation.

All controls to be panel mounted and so located on the boiler as to provide ease of servicing the boiler without disturbing the controls and also located to prevent possible damage by water according to UL and CSA requirements.

Electrical power supply shall be 115 volts, 60 cycle single phase.

When multiple boilers are to be installed together, a system integration control shall be provided to stage up to 8 boilers.  The control shall include automatic selection of needed boilers based on energy demand, an adjustable outdoor reset schedule, domestic hot water priority, and a system digital display.  The control shall stage and modulate the boilers utilizing firing rate threshold staging and parallel modulation to optimize condensing potential while minimizing energy wasting short cycling.  This strategy takes full advantage of the inverse efficiency characteristic (lower fire rate, higher efficiency) of condensing boilers.  The control shall monitor supply water temperature, return water temperature and shall communicate between boilers via RS-485 network wiring.

Boilers shall communicate with [BACnet I/P] [BACnet MSTP] [LONWorks] [ModBus TCP/IP] [ModBus RTU] [Johnson Metasys N2] building management system utilizing a protocol translator for requirements other than the native ModBus RTU.

The Protocol Translator solution can either come factory mounted in a NEMA 1 enclosure, or ship loose for installation in a boiler control panel. Select the option below that applies.

Protocol translator mounted in a NEMA 1 panel with power supply and terminals.

Protocol translator shipped loose for installation in boiler control panel with required power supply.

The boiler controls shall include provisions for [outside air reset] [night setback].

The boiler controls shall include provisions for sending signal to [start/stop primary boiler pump] [start/stop primary boiler pump and vary pump speed based on boiler firing rate] [open/close automatic isolation valve].

ELECTRICAL POWER

Single-Point Field Power Connection: Factory-installed and -wired electrical devices necessary shall provide a single-point field power connection to boiler. Separate power and control connections will not be allowed.

House in NEMA 250, Type 1 enclosure.

Wiring shall be numbered and color coded to match wiring diagram.

Install factory wiring outside of an enclosure in a metal raceway or conduit.

Select disconnect option below if disconnect is to be provided with boiler. If by others, delete item below.

Field power interface shall be to non-fused disconnect switch.

VENTING

Exhaust Stack: Complete system, per UL 1738 for Category IV appliances, stainless steel, pipe, vent terminal, thimble, vent adapter, and sealant.

Stack to be designed and manufactured by boiler manufacturer.

Combustion-Air Intake: Complete system, [PVC] [galvanized steel] [spiral duct] [stainless steel], pipe, vent terminal with screen, inlet air coupling, and sealant, by others.

SOURCE QUALITY CONTROL

Burner and Hydrostatic Test: Factory pressure test gas train, test fire burner and gas train assembly, and perform a functional controls test for all safety devices; perform hydrostatic test.

Test and inspect factory-assembled boilers, before shipping, according to most current ASME Boiler and Pressure Vessel Code.

EXECUTION

BOILER INSTALLATION

Installation shall be provided by the contractor in accordance with the requirements of the codes specified hereinbefore.  All of the contractor's work shall be performed by experienced personnel previously engaged in boiler plant construction and shall be under the supervision of a qualified installation supervisor.

Equipment Installation:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases. The CFC-E boiler is not required to be installed on a concrete pad.

Install boilers on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases.

Retain paragraph 2 below for projects requiring seismic restraints.

Comply with requirements for seismic-restraint devices.

Install equipment in strict compliance with manufacturer's installation instructions.

Install equipment in strict compliance with state and local codes and applicable NFPA standards.

Maintain manufacturer's recommended clearances around sides and over top of equipment.

Install components that were removed from equipment for shipping purposes.

Install components that were furnished loose with equipment for field installation.

Provide all interconnecting electrical control and power wiring.

Provide all fuel gas vent and service piping.

Provide all piping for boiler pipe connections.

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

Install piping adjacent to boiler to allow service and maintenance.

Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

Connect gas piping to boiler gas-train inlet with union. Piping shall be at least full size of gas-train connection. Provide a reducer if required. Piping shall be properly sized to minimize pressure drops for longer gas piping runs. Refer to boiler IOM for sizing and header recommendations.

Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Install piping from safety relief valves to nearest floor drain.

Boiler Venting:

Install flue venting and combustion-air intake.

Ground equipment according to specification requirements.

Connect wiring according to specification requirements.

FIELD QUALITY CONTROL

General:  The boiler supplier’s factory authorized service organization shall be responsible for performance of inspections, start up and testing of the package boiler, and accessory equipment and materials furnished under this Section.  A detailed written record of the startup performance, including burner setting data over the entire load range shall be furnished to the engineer before final acceptance. All labor, equipment, and test apparatus shall be furnished by the authorized service organization.  All equipment defects discovered by the tests shall be rectified either by the service organization or boiler manufacturer.

Equipment inspection:  Boiler representative shall inspect boilers and other equipment upon arrival, verifying completeness of equipment supplied and potential damages. All shipped loose components, to be mounted and installed on boiler by contractor.

Equipment shall be flushed prior to start-up per the water treatment company guidelines and product installation manual requirements.

Pre start-up walk through: Boiler representative shall review the installation with the mechanical contractor prior to start-up and note any required changes prior to start-up.

Start-up shall be conducted by experienced and factory authorized technician in the regular employment of the authorized service organization, and shall include:

1.	Demonstrate that boiler, burner, controls, and accessories comply with requirements of this Section as proposed by the boiler and accessories supplier.  Pre-test all items prior to scheduling the final testing that will be witnessed by the test engineer.

2.	Readings at different firing rates (20, 50, 75 and 100%) of load for the modulating burner shall be taken with a written report of the tests submitted to the engineer.  The reports shall include readings for each firing rate tested and include stack temperatures, O2, CO, NOx, and overall boiler efficiency.

3.	Auxiliary Equipment and Accessories:  Observe and check all valves, draft fans, electric motors and other accessories and appurtenant equipment during the operational and capacity tests for leakage, malfunctioning, defects, and non-compliance with referenced standards or overloading as applicable.

4.	Commissioning Requirements:

      - Fireside inspection

      - Set up fuel train and combustion air system

      - Set up operating set points

      - Check all safeties, including Flame safeguard, LWCO, Airflow, Fuel pressures, High limits.

      - Set up and verify efficiencies at 20%, 50%, 75%, and 100%

      - Set up and verify burner turndown.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

DEMONSTRATION

Training to include all safety procedures, maintenance procedures, control operations, and diagnostic procedures.  Training to be provided in a single ____ hour continuous session to accommodate operator’s availability on site.

END OF SECTION 235216